## Table A.2
Table A.2 – Ranges of 90 % typical gas concentration values observed in power transformers
Values in microlitres per litre
| C2H2 | H2 | CH4 | C2H4 | C2H6 | CO | CO2
All transformers |  | 50 to 150 | 30 to 130 | 60 to 280 | 20 to 90 | 400 to 600 | 3 800 to 14 000
No OLTC | 2 to 20
Communicating OLTC | 60 to 280

## Table A.4
Table A.4 – Examples of 90 % typical concentration values observed on individual networks
Values in microlitres per litre
Transformer subtype | H2 | CO | CO2 | CH4 | C2H6 | C2H4 | C2H2
Furnace | 200 | 800 | 6000 | 150 | 150 | 200 | a
Distribution | 100 | 200 | 5000 | 50 | 50 | 50 | 5
Submersible | 86 | 628 | 6295 | 21 | 4 | 6 | < S b
NOTE The values listed above were obtained from one particular network. Values on other networks can differ.
a The data are influenced by the design and assembly of the on-load tap-changer. For this reason, no statistically significant value can be proposed for acetylene.
b < S means less than the detection limit.